|  | DBSF-1... | DBSF-3E...6E | DBSF-2...PL |
| --- | --- | --- | --- |
| LIQUID FLOW SWITCHES | DBSF-1K/40 |  |  |

DBSF

| FUNCTION |  |  |  | APPLICATIONS |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Flow control of aggressive media, water and normal media | Well-suited in pipes of general industrial plants: |  |
| (depending on model). |  |  | - heating and air conditioning systems; |  |
| Alarm signal of flow shortage (safety switch). |  | - | refrigeration systems; |  |  |  |
| Available in brass, suitable for normal media, and in stainless | - sprinkler or anti-fire systems; |  |
| steel AISI316L, suitable for sea water and aggressive media. | - | heat pumps; |  |  |  |
|  |  |  |  | - devices for oil monitoring; |  |  |  |
|  |  |  |  | - | lubrification circuits. |  |  |  |
| TYPE | PIPE | MAX | NORMAL | AGRESSIVE | BODY WITH | PROTECTION |  | FLOW |
|  |  | PRESSURE | MEDIA |  | MEDIA | PIPE FITTING |  |  | RATE |
|  | Ø | bar | (body in brass) | (body in stainless | “T” |  |  |  |
|  |  |  |  | steel AISI 316L) |  |  |  |  |
| DBSF-1K | 1…8“ | 11 | • |  |  |  | IP65 |  | 1 |
| DBSF-1K/40 | 1…8“ | 11 | • |  |  |  | IP40 |  | 1 |
| DBSF-1K/NPT | 1…8“ | 11 | • |  |  |  |  |  | 1 |
| DBSF-1KPL | 1…8“ | 11 | • |  |  |  |  |  | 1 |
| DBSF-1E* | 1…8“ | 11 | • |  |  |  | IP65 |  | 1 |
| DBSF-1EPL* | 1…8“ | 11 | • |  |  |  |  |  | 1 |
| DBSF-1RE | 1…8“ | 11 | • |  |  |  | IP65 |  | 2 |
| DBSF-2E** | 1…8“ | 30 |  |  | • |  | IP65 |  | 1 |
| DBSF-2EPL** | 1…8“ | 30 |  |  | • |  |  |  | 1 |
| DBSF-2RE | 1…8“ | 30 |  |  | • |  | IP65 |  | 2 |
| DBSF-2REPL | 1…8“ | 30 |  |  | • |  |  |  | 2 |
| DBSF-3E | 1/2“ | 11 | • |  |  | • | IP65 |  | 3 |
| DBSF-4E | 3/4“ | 11 | • |  |  | • | IP65 |  | 3 |
| DBSF-6E | 1“ | 11 | • |  |  | • | IP65 |  | 3 |

NPT	1” NPT connector

PL	ABS cover, Byblend base (IP65)

- models with TÜV approval (S 04-025) ** models with TÜV approval (S 02-026)

| TECHNICAL FEATURES |  |
| --- | --- |
| Contacts: | dust-tight microswitch with switching |
|  | contacts (n.c./n.o.) |
| Switch capacity: | 15 (8) A, 24...250 Vac |
| Working: | -40...+85 °C |
|  | 10...90% r.h. (non condensing) |
| Max liquid | -40...+120 °C |
| temperature: |  |
| Max pressure: | 11 bar (DBSF-2: 30 bar) |
| Fitting: | see flow rate schedule |
| Body: | see schedule above |
| Paddles: | stainless steel AISI 316L |
| Housing: | galvanized steel sheet plate, ABS cover |
|  | version PL: Byblend base, ABS cover |
| Protection: | IP65, class I |
| Size: | 113 x 70 x 65 mm |
|  | version PL: 108 x 70 x 72 mm |
| Peso: | 950 g |

148

LIQUID FLOW SWITCHES	DBSF

- H2O FLOW RATE

DBSF-1K/DBSF-1E/DBSF-2E

| Pipe | Qmax | Min. | Max. |
| --- | --- | --- | --- |
| connector | m3/h | adjustment | adjustment |
| ± | recommended | m3/h | m3/h |
|  |  | cut-off | cut-off |
|  |  | (cut-in) | (cut-in) |
| 1“ | 3,6 | 0,6 (1,0) | 2,0 (2,1) |
| 1 1/4“ | 6,0 | 0,8 (1,3) | 2,8 (3,0) |
| 1 1/2“ | 9,0 | 1,1 (1,7) | 3,7 (4,0) |
| 2“ | 15,0 | 2,2 (3,1) | 5,7 (6,1) |
| 2 1/2“ | 24,0 | 2,7 (4,0) | 6,5 (7,0) |
| 3“ | 36,0 | 4,3 (6,2) | 10,7 (11,4) |
| 4“ | 60,0 | 11,4 (14,7) | 27,7 (29,0) |
| 4“ Z | 60,0 | 6,1 (8,0) | 17,3 (18,4) |
| 5“ | 94,0 | 22,9 (28,4) | 53,3 (55,6) |
| 5“ Z | 94,0 | 9,3 (12,9) | 25,2 (26,8) |
| 6“ | 120,0 | 35,9 (43,1) | 81,7 (85,1) |
| 6“ Z | 120,0 | 12,3 (16,8) | 30,6 (32,7) |
| 8“ | 240,0 | 72,6 (85,1) | 165,7 (172,5) |
| 8“ Z | 240,0 | 38,6 (46,5) | 90,8 (94,2) |

For models with suffix “Z” the longest paddle must be used to obtain the values indicated on the table.

Pressure drop at the maximum flow (Qmax): 0,08 bar

3

FLOW RATE WITH ıT„ PIPE FITTING

DBSF-3E /-4E /-6E

| DBSF- | Pipe connector | Min. | Max. |
| --- | --- | --- | --- |
|  | with ıT„ | adjustment | adjustment |
|  | pipe fitting |  |  |  |  |
|  | ± | m3/h | m3/h |
|  |  | cut-off | cut-off |
|  |  | (cut-in) | (cut-in) |
| 3E | 1/2“ | 0,174 | (0,48) | 0,846 | (0,948) |
| 4E | 3/4“ | 0,138 | (0,408) | 0,768 | (0,858) |
| 6E | 1“ | 0,2 | (0,6) | 1,0 | (1,1) |

The “T” connectors have cylindrical GAS thread.

- H2OF LOW RATE

DBSF-1RE/DBSF-2RE

| Pipe | Min. | Max. |
| --- | --- | --- |
| connector | adjustment | adjustment |
| ± | m3/h | m3/h |
|  | cut-off | cut-off |
|  | (cut-in) | (cut-in) |
| 1“ | 0,2 (0,6) | 1,0 (1,1) |
| 1 1/4“ | 0,25 (0,9) | 1,4 (1,6) |
| 1 1/2“ | 0,5 (1,2) | 1,6 (2,2) |
| 2“ | 0,9 (2,3) | 3,6 (4,1) |
| 2 1/2“ | 1,2 (3,1) | 4,9 (5,5) |
| 3“ | 2,1 (4,9) | 7,4 | (8,2) |
| 4“ | 4,9 (11,3) | 17,1 | (19,1) |
| 4“ Z | 3,3 (7,7) | 11,6 (13,0) |
| 5“ | 9,7 (22,4) | 34,0 (37,9) |
| 5“ Z | 5,0 (11,5) | 17,5 | (19,6) |
| 6“ | 13,6 (31,5) | 47,6 | (53,2) |
| 6“ Z | 6,1 (14,1) | 21,4 | (23,9) |
| 8“ | 25,7 (59,6) | 90,1 (100,7) |
| 8“ Z | 21,7 (36,5) | 55,3 (61,8) |

Paddles (models without “T” pipe fitting)

| PIPE | PADDLES |
| --- | --- |
| 1” | 1 |
| 1 1/4” | 1 |
| 1 1/2” | 1 |
| 2” | 1,2 |
| 2 1/2” | 1,2 |
| 3” | 1,2,3 |
| 4” | 1,2,3 |
| 4” Z | 1,2,3,4 |
| 5” | 1,2,3 |
| 5” Z | 1,2,3,4 |
| 6” | 1,2,3 |
| 6” Z | 1,2,3,4 |
| 8” | 1,2,3 |
| 8” Z | 1,2,3,4 |

149

LIQUID FLOW SWITCHES

| ELECTRICAL WIRING |  |  |  |  | DIMENSIONS (mm) |
| --- | --- | --- | --- | --- | --- |
| Diagram during flow presence. |  |  |  |  | DBSF |

earth

fig. 1

Adjustment screw for flowrate

Connect the red and the white contacts of the microswitch (fig. 1).

The contact red-white opens when the flow drops below the set

level.

When the flow is missing the contact red-blue closes and can be

used as a signal or alarm contact.

INSTALLATION	DBSF/PL

The flowswitch can installed in every position far from elbows or

throttlings, with arrow on flow direction. If pipe is vertical, recali-

brate range to balance paddle weight. If the device is downwards

mounted take care to slags, and apply it in a straight pipe far from

filters, valves, etc with length at least 5 times the diameter of pipe

upstream and downstream the unit.

NOTE

The flowswitch is factory calibrated at its min. sensitivity. To increase

the set value turn clockwise the adjustment screw. The cut-out value

must be >- the minimum flow necessary to guarantee the protection

of the plant. The units without “T” fittings are supplied with 4 paddles,

which must be cut off according to the pipe. All devices can be sup-

plied with “T” connection on request as schedule indications.

ATTENTION

If flowswitch is used as a minimum flow controller, it is neces-

sary to add another device downstream for alarm condition

activation.

DBSF

L	changeable length (see the drawing of the paddles)

150